## Hoja1
id_simulacion | 10 | 1007
n_pv | 190 | 405
n_dg | 1 | 1 | Input | Symbol | Value |  | Input | Symbol | Value
p_dg | 10 | 0 | Positive battery constant | $Mb$ | 0.01 |  | Maximum Power $Wp$ | $Ppv_{stc}$ | 300
min_dg | 0.9 | 0 | Self-Discharge rate | $\sigma$ | 0.2 |  | Module Efficiency $(\%)$ | $\eta _{pv}$ | 18.33
efi_dg | 1 | 1 | Capacity Rate $(h)$ | $Crate$ | 5 |  | $NOCT (\circle^C)$ | $NOCT$ | 45
lpsp | 0.05 | 0.05 | Maximum depth of discharge $(\%)$ | $DOD^{max}$ | 0.5 |  | Price per kWh generated $(USD/kWh)$ | $cpv$ | 0.003
p_bat | 40.32 | 100.8 | Maximum number of cycles | $cycles^{max}$ | 3000 |  | Photovoltaic derating factor $(\%)$ | $fpv$ | 85
cond_init_bat | 40.32 | 100.8 | Price per kWh generated $(USD/kWh)$ | $cbat$ | 0.11855 |  | $O\&M$ factor of the initial investment $(\%)$ | $\rho _{pv}$ | 1
val_aux_bateria | 0.01 | 0.01 | Battery cell capacity $(kWh)$ | $Pbat_{cell}$ | 0.84 |  | Price per kW installed $(USD/kWh)$ | $cki_{pv}$ | 1.5
DOD | 0.5 | 0.5 | DC system voltage (V) | $Vdc_{sist}$ | 48 |  | Power Temperature Coefficient $(%/\circle^C)$ | $\alpha _{p}$ | -0.39
n_bat | 1 | 1 | Battery Voltage (V) | $Vdc_{bc}$ | 2
self_dis_coef | 0.2 | 0.2 | Inverter efficiency $(\%)$ | $\eta _{inv}$ | 95
max_ciclos_descarga | 3000 | 3000 | $O\&M$ factor of the initial investment $(\%)$ | $\rho _{bat}$ | 2
efficiency_inversor | 0.95 | 0.95 | Factor of the initial capital cost invested $(\%)$ | $\lambda _{bat}$ | 70
efficiency_charging | 0.9 | 0.9 | Lifecycle $(years)$ | $Lc_{bat}$ | 10
C_rate | 5 | 5 | Price per kWh installed $(USD/kWh)$ | $cki_{bat}$ | 61.4
cost_pv | 10 | 10 | Discharge efficiency $(\%)$ | $\eta _{d}$ | 100
cost_dg | 824 | 824 | Charge efficiency $(\%)$ | $\eta _{c}$ | 90
cost_bat | 443 | 443
cost_pens | 1533 | 1533
optimizacion | optimal | optimal
lpsp_result | 5 | 4.99 | Input | Symbol | Value
ens_result | 1823.3 | 1821.2 | Life time of the project $(years)$ | $R$ | 20
ciclos_bat_result | 229.1 | 116.3 | Maximum loss of power supply probability $(\%)$ | $LPSP^{max}$ | 5
vida_proyecto | 20 | 20 | Real interest rate $(\%)$ | $ir$ | 8.08
ir | 0.0808 | 0.0808 | Cost of energy not supplied $(USD/kWh)$ | $cpens$ | 0.7434
crf | 0.1 | 0.1 | fiscal_incentive_factor $(\%)$ | $\delta$ | 90.38
cpv_ins | 5605.365 | 5605.365
cbat_ins | 539983.495 | 539983.495
cdg_ins | 7627407.001 | 7627407.001
capital_cpv | 319505805 | 681051847.5
capital_cbat | 21772134.5184 | 54430336.296
capital_cdg | 76274070.01 | 0
kbat | 0.6712 | 0.6712
kdg | 0.6712 | 0.6712
ybat | 0.7 | 0.7
ydg | 0.7 | 0.7
rc_bat | 10229419.6821 | 25573549.2053
rc_dg | 35836609.0535 | 0
factor_bat | 0.02 | 0.02
factor_pv | 0.01 | 0.01
oym_pv | 3195058.05 | 6810518.48 | Input | Symbol | Value
oym_bat | 435442.69 | 1088606.73 | DG Power (kW) | $Pdg^{rate}$ | 10
ipp_actual | 129.23 | 129.23 | Price per kWh installed $(USD/kWh)$ | $cki_{dg}$ | 95.5
trm | 3736.91 | 3736.91 | Minimum ratio allowed | $\gamma$ | 0.9
pami | 8789 | 8789 | Diesel efficiency $(\%)$ | $\eta_{dg}$ | 100
plim | 79900 | 79900 | Price per kWh generated $(USD/kWh)$ | $cdg$ | 0.22
oym_dg | 14958813.62 | 0 | Factor of the initial capital cost invested $(\%)$ | $\lambda _{dg}$ | 70
asc | 17380.97 | 22479.72 | Specific consumption of fuel $(gal/kWh)$ | $scf$ | 0.0974
lcoe | 0.5 | 0.84 | Specific consumption of Lubricant $(gal/kWh)$ | $scl$ | 0.0005
asc_incentivo | 16502.41 | 20586.36 | Lifecycle $(years)$ | $Lc_{dg}$ | 10
lcoe_incentivo | 0.48 | 0.77 | Average price of Lubricant $(Usd/gal)$ | $alc$ | 21.4
cost_e_dg | 3010.81 | 0 | Average price of fuel $(Usd/gal)$ | $afc$ | 2.4
cost_e_pv | 67.17 | 90.18
cost_e_bat | 1094.88 | 1090.1
cost_e_ens | 1355.4412 | 1353.93
|  |  | Parameter | Unit | PV-BAT-DG | PV-BAT
|  |  | $Npv$ | Units | 190 | 405
|  |  | $Nbat$ | Units | 48 | 120
|  |  | $Nbat_{p}$ | Units | 2 | 5
|  |  | $Ebatn$ | $kW$ | 40.32 | 100.8
|  |  | $LC$ | $Number$ | 229 | 116.3
|  |  | $Pdg$ | $kW$ | 10 | -
|  |  | $CCpv$ | $USD$ | 85500 | 182250
|  |  | $CCbat$ | $USD$ | 5826.24 | 14565.6
|  |  | $CCdg$ | $USD$ | 20411 | -
|  |  | $O\&Mpv$ | $USD/year$ | 855 | 1822.5
|  |  | $O\&Mbat$ | $USD/year$ | 116.5248 | 291.312
|  |  | $O\&Mdg$ | $USD/year$ | 4002.9901 | -
|  |  | $RCbat$ | $USD$ | 2737.4006 | 6843.5015
|  |  | $RCdg$ | $USD$ | 9589.9042 | -
|  |  | $LPSP$ | $\%$ | 5 | 9.9
|  |  | $CRF$ | $\%$ | 10 | 10
|  |  | $PENS$ | $kWh/year$ | 1823.3 | 1821.2
|  |  | $Cost_{ENS} | $USD/year$ | 1355.4412 | 1353.93
|  |  | $ASC$ | $USD/year$ | 17380.97 | 22479.72
|  |  | $LCOE$ | $USD/year$ | 0.5 | 0.84
|  |  | $\deltaASC$ | $USD/year$ | 16502.41 | 20586.36
|  |  | $\deltaLCOE$ | $USD/year$ | 0.48 | 0.77

## Hoja2
58 | 420 | 1 | 0 | 0 | 1 | 0.1 | 67.2 | 67.2 | 0.01 | 0.5 | 1 | 0.2 | 1500 | 0.95 | 0.9 | 5 | 10 | 824 | 443 | 1533 | optimal | 9.99 | 3644.4 | 145.3 | 20 | 0.0808 | 0.1 | 5605.365 | 539983.495 | 7627407.001 | 706275990 | 36286890.864 | 0 | 0.6712 | 0.6712 | 0.7 | 0.7 | 17049032.8035 | 0 | 0.02 | 0.01 | 7062759.9 | 725737.82 | 129.23 | 3736.91 | 8789 | 79900 | 0 | 22411.48 | 0.32 | 20499.89 | 0.3 | 0 | 205.14 | 2315.59 | 4751.58
1007 | 405 | 1 | 0 | 0 | 1 | 0.05 | 100.8 | 100.8 | 0.01 | 0.5 | 1 | 0.2 | 3000 | 0.95 | 0.9 | 5 | 10 | 824 | 443 | 1533 | optimal | 4.99 | 1821.2 | 116.3 | 20 | 0.0808 | 0.1 | 5605.365 | 539983.495 | 7627407.001 | 681051847.5 | 54430336.296 | 0 | 0.6712 | 0.6712 | 0.7 | 0.7 | 25573549.2053 | 0 | 0.02 | 0.01 | 6810518.48 | 1088606.73 | 129.23 | 3736.91 | 8789 | 79900 | 0 | 22479.72 | 0.84 | 20586.36 | 0.77 | 0 | 90.18 | 1090.1 | 1353.93